## NCTS-R6K192
NEW COMPUTER TECHNOLOGY SYSTEMS (NCTS) LIMITED COMPANY
新计算机科技系统（NCTS）有限公司
深圳市龙岗区布吉诚信华庭2栋6B
www.ncts.co
MODEL | NCTS-R6K192
PICTURE
Rack-Mounted UPS
Capacity :6000va / 4800w
● True double-conversion online UPS ● Micro processor control optimizes reliability ● Output power factor 0.8 ● Wide Input voltage range(110V – 300VAC) ● Input power factor correction ● Converter mode available ● ECO mode for energy saving ● Generator compatible ● Smart SNMP works well with either USB or RS-232 together ● Comprehensive display allows easy monitoring and access of UPS status ● True Isolation technology offers the most complete power protection and highest quality power for all IT applications. ● SNMP Slots for remote monitoring and control ● Load sensing, overload protection, dynamic by-pass, temperature monitoring software for preventative diagnostics. ● LED / LCD option ● Extended backup time capacity ● Zero transfer time
Rated capacity | 6KVA / 4.8KW
Format | 3U
Input Voltage Range | 120 - 275 VAC ± 5
Input Frequency Range | (45 -55) ± 0.5Hz
Input Bypass Range | 80VAC x (1 ± 5%) – 285VAC x (1 ±5%)
BATTERY Voltage | 192VDC
BATTERY Capacity and Quantity | External battery
BATTERY charge current | 4A
Output Voltage | 220VAC ± 1% (invert output)
Output Frequency | 46 - 54Hz (normal AC output); 50Hz ± 1% (abnormal AC output)
Output Wave Form | Sine wave THD < 3% (linear load); sine wave THD <8% (nonlinear load)
Overload | 105 - 125%: convert to byass after 1 minute
Output Power Factor | 0.8
Output Current Peak Factor | 3 : 1
Communication & monitoring | RS232 / USB+software+cable , SNMP slot
N.G. (KG) | 18.5
Unit size | 482.6*600*133m
Package Size (mm) | 725*530*180
Application area | OFFICE, IT ROOM, INDUSTRIAL ENVIRONMENT, Security and Protection System, Communication System and Computer Network System
Certification | ISO9001, ISO14001, CE, ROHS